DC POWER + WIRELESS LIGHTING CONTROLS

COMMERCIAL APPLICATIONS GUIDE

Conceptual Design Edition | August 2026

A room-by-room design guide for direct-current lighting distribution, wireless occupancy/daylight sensing, self-powered wall controls, and integration into the Symple Buildings digital building platform.

DESIGN INTENT

Reduce branch-conversion losses, simplify room controls, expose circuit-level power data, and standardize repeatable commercial space applications.

CONCEPTUAL - NOT FOR CONSTRUCTION

| CONTENTS + GUIDE INTENT | INTRODUCTION |
| --- | --- |

# How to use this guide

This guide follows the room-by-room application pattern used by leading commercial lighting-control guides: each application shows a conceptual layout, control sequence, recommended control strategies, and a basis-of-design component set. It is intended for early design, sales engineering, estimating, and coordination - not as a substitute for project electrical drawings, product listings, or local code requirements.

| # | Section | Purpose |
| --- | --- | --- |
| 1 | Platform overview | DC distribution + control architecture |
| 2 | Design rules | Circuiting, zoning, controls, commissioning |
| 3 | Private office | Manual dimming + occupancy + daylight |
| 4 | Open office | Multi-zone + daylight + occupancy |
| 5 | Conference room | Scenes + presentation mode |
| 6 | Classroom / training | Two-zone teaching + daylight |
| 7 | Break room | Vacancy-oriented control |
| 8 | Restroom | Occupancy automatic-off |
| 9 | Egress corridor | Reduced level / occupied response |
| 10 | Egress stairwell | Safe reduced-level strategy |
| 11 | Atrium / lobby | Large-area zoning + schedules |
| 12 | Schedules + commissioning | BOM and startup checklist |

## Control philosophy

DC power is centralized and monitored; room-level loads are distributed as low-voltage DC branches appropriate to the listed equipment and project wiring method.

Occupancy, ambient light, wall control, scenes, and scheduling are software-defined wherever supported, minimizing dedicated control wiring.

Each space is designed as a repeatable application package with clear zones, a sequence of operation, and commissioning settings.

Life-safety and emergency lighting functions remain subject to the project emergency-power strategy, product listings, and authority having jurisdiction.

| PLATFORM OVERVIEW | SYSTEM ARCHITECTURE |
| --- | --- |

# A DC-first lighting and controls platform

The Symple Buildings concept combines centralized intelligent DC power distribution with wireless room controls and a supervisory digital-building layer. The power and control planes are intentionally separated: lighting power remains on monitored DC branches while room behavior can be configured through wireless controls and software.

| Layer | Basis-of-design | Application value |
| --- | --- | --- |
| DC distribution | EPS IPS-32: 32 outputs, 56 VDC, 100 W/output | Centralized conversion, per-port status, remote reset/control, grouped outputs |
| Presence/daylight | Casambi NASSR PDS-BAT-CAS PIR + ambient light sensor | Wireless occupancy/vacancy logic and light-level sensing |
| Wall control | mwConnect PSC-EO-WS BLE self-powered controller | Batteryless manual on/off, dimming, scenes / tunable-white control where supported |
| Room topology | SmartDC-style low-voltage branch / network architecture | Repeatable room nodes, sensors, relays/controllers and DC luminaire circuits |
| Supervisory layer | Symple Buildings integration | Schedules, diagnostics, energy data, APIs/BMS gateways - project specific |

| DESIGN RULES | BASIS OF DESIGN |
| --- | --- |

# Core electrical + controls rules

## 1. Zone the room before choosing devices

Define general, perimeter/daylight, task/whiteboard, presentation, and egress zones first. Tie DC branch grouping and control logic to these functional zones.

## 2. Keep power distribution observable

Assign IPS-32 output labels by floor/room/zone. Use linked output groups only where the loads are intended to operate together.

## 3. Use wireless controls to reduce control wiring

Place occupancy/daylight sensors for coverage and self-powered wall controls at natural entry points. Verify the exact controller/profile compatibility before procurement.

## 4. Treat daylight as a distinct control layer

Perimeter fixtures should be separately controllable so ambient-light sensing can trim only the zone receiving useful daylight.

## 5. Preserve local control

Even when schedules/BMS are present, occupants should retain intuitive local control where appropriate. Central schedules should set defaults, not create confusing overrides.

## 6. Commission the sequence, not just the devices

Document manual-on/auto-on choice, timeout, fade, high-end trim, sensor sensitivity, daylight target, scene levels, and post-power-failure startup behavior.

## 7. Separate concept from compliance

Conductor size, circuit classification, emergency lighting, plenum rules, overcurrent protection, voltage drop, and product listing requirements must be engineered for the specific project.

Compatibility checkpoint: The uploaded Casambi sensor is explicitly a Casambi 2.4 GHz BLE-based proprietary mesh device. The mwConnect wall control is a Bluetooth self-powered controller that must pair with a compatible device/node. This guide treats them as basis-of-design controls, but the final room controller must be selected and validated so both intended control inputs are supported.

| PRIVATE OFFICE | APPLICATION |
| --- | --- |

Application intent: Best default package for repeatable offices: one sensor, one wireless wall station, and a small DC lighting branch.

| CONTROL STRATEGIES | SEQUENCE OF OPERATION |
| --- | --- |
| Manual-on / auto-off occupancy Personal dimming Daylight trim at perimeter High-end trim | Entry: lights remain off until the occupant presses the wall control (preferred vacancy mode). Occupied: wall control raises/lowers the general zone; perimeter zone is trimmed by available daylight. Vacant: occupancy sensor starts the programmed delay; all non-required lighting turns off after timeout. After power restoration: IPS-32 port startup behavior returns the room to the approved default state. |

## Basis-of-design equipment

| Qty | Element | Design basis |
| --- | --- | --- |
| 1 | IPS-32 output | 56 VDC branch assigned to room lighting |
| 1 | Room / fixture controller | DC dimming output compatible with selected luminaires |
| 1 | PIR + ambient sensor | Casambi NASSR PDS-BAT-CAS |
| 1 | Self-powered wall control | mwConnect PSC-EO-WS-100-BLE or compatible profile |
| 4 typ. | DC LED luminaires | One or two control zones |

| OPEN OFFICE | APPLICATION |
| --- | --- |

Application intent: Use distributed sensing and explicit perimeter zoning rather than a single floor-wide occupancy signal.

| CONTROL STRATEGIES | SEQUENCE OF OPERATION |
| --- | --- |
| Occupancy by area Perimeter daylight harvesting Multi-zone dimming Scheduling / after-hours sweep Demand reduction ready | Business hours: schedule enables the floor while occupancy sensors control local areas. Occupied areas: general zones rise to the commissioned level; perimeter rows trim independently with daylight. Unoccupied pockets: local zones reduce/off after timeout without shutting down the entire office. After hours: schedule drives an off state; local controls can provide timed override where approved. |

## Basis-of-design equipment

| Qty | Element | Design basis |
| --- | --- | --- |
| 1+ | IPS-32 outputs | Multiple 56 VDC branches by lighting zone |
| 3 typ. | Room/zone controllers | General + perimeter + support zones |
| 2-4 | PIR + ambient sensors | Coverage coordinated with workstation layout |
| 2+ | Self-powered wall controls | Entry + collaboration/support areas |
| 12+ | DC LED luminaires | Grouped by daylight and occupancy zones |

| CONFERENCE ROOM | APPLICATION |
| --- | --- |

Application intent: Conference rooms benefit from scene logic; use a dual-channel/scene input and separate front-of-room lighting.

| CONTROL STRATEGIES | SEQUENCE OF OPERATION |
| --- | --- |
| Scene control Occupancy auto-off Presentation mode Personal dimming Optional tunable white | Entry: wall station selects General, Presentation, Video, or Off scene. Presentation: front/screen zone reduces while table/perimeter lighting remains at the commissioned level. Occupied: manual scene changes remain available; occupancy holds the room active. Vacant: all normal lighting returns to off after the programmed timeout. |

## Basis-of-design equipment

| Qty | Element | Design basis |
| --- | --- | --- |
| 1 | IPS-32 output/group | Room lighting DC branch |
| 1-2 | Dual-channel / scene controllers | Scene-capable dimming outputs |
| 1 | PIR + ambient sensor | Ceiling mounted |
| 1 | Dual-rocker self-powered control | PSC-EO-WS-400-BLE for scenes / two-channel use where supported |
| 6 typ. | DC LED luminaires | At least two independently controlled zones |

| CLASSROOM / TRAINING | APPLICATION |
| --- | --- |

Application intent: Keep the front teaching zone independent from the daylight perimeter so instruction remains visually consistent.

| CONTROL STRATEGIES | SEQUENCE OF OPERATION |
| --- | --- |
| Two-zone teaching control Occupancy auto-off Daylight trim High-end trim Scene presets | Entry: instructor enables the room from the wall station. Teaching: general zone and front/whiteboard zone are independently dimmable. Daylight: window-side fixtures trim to maintain the commissioned target without affecting front-of-room visibility. Vacant: lighting turns off after timeout; scheduled shutdown provides a secondary sweep. |

## Basis-of-design equipment

| Qty | Element | Design basis |
| --- | --- | --- |
| 1-2 | IPS-32 outputs | General + front/whiteboard branches |
| 2 | Control channels | Independent teaching zones |
| 1-2 | PIR + ambient sensors | Coverage based on room size |
| 1 | Scene / dual-channel wall control | Two-zone or scene input |
| 8 typ. | DC LED luminaires | General + front + optional perimeter subgroup |

| BREAK ROOM | APPLICATION |
| --- | --- |

Application intent: Simple vacancy control delivers most of the benefit with minimal hardware.

| CONTROL STRATEGIES | SEQUENCE OF OPERATION |
| --- | --- |
| Manual-on / auto-off Occupancy sensing Simple dimming Scheduling | Entry: occupant presses wall control to turn on lighting, or auto-on may be used if preferred by the owner. Occupied: lighting remains at the commissioned setpoint with local dimming available. Vacant: lights turn off after a short timeout. After hours: central schedule keeps the space off except for approved local override. |

## Basis-of-design equipment

| Qty | Element | Design basis |
| --- | --- | --- |
| 1 | IPS-32 output | Single DC branch |
| 1 | Room controller | Single-zone dimming |
| 1 | PIR sensor | Ceiling coverage |
| 1 | Self-powered wall control | Single rocker |
| 4 typ. | DC LED luminaires | Single zone |

| MULTI-STALL RESTROOM | APPLICATION |
| --- | --- |

Application intent: Sensor placement is the critical design variable because partitions can block PIR coverage.

| CONTROL STRATEGIES | SEQUENCE OF OPERATION |
| --- | --- |
| Occupancy auto-on / auto-off Full-room coverage Optional reduced standby level | Entry: occupancy triggers the normal lighting level. Occupied: lights remain on while presence continues; use enough sensors to cover stalls and entry/handwashing zones. Vacant: lighting turns off or returns to a permitted reduced level after timeout. No routine wall control is required unless the project standard calls for one. |

## Basis-of-design equipment

| Qty | Element | Design basis |
| --- | --- | --- |
| 1 | IPS-32 output | Restroom lighting branch |
| 1 | Room controller | Switching or dimming output |
| 1-2 | PIR sensors | Coverage verified around partitions |
| 4 typ. | DC LED luminaires | Single or two-zone layout |

| EGRESS CORRIDOR | APPLICATION |
| --- | --- |

Application intent: Design corridor zoning around travel direction and sensor handoff so users do not enter a dark section.

| CONTROL STRATEGIES | SEQUENCE OF OPERATION |
| --- | --- |
| Occupancy response Reduced unoccupied level Scheduling Emergency-state coordination | Normal occupied period: corridor remains at the programmed normal or code-permitted reduced level. Presence: sensor raises the affected corridor section to the occupied target. No presence: lighting returns to the approved reduced/off state after timeout. Emergency: emergency/egress behavior is controlled by the project life-safety design, not by normal wireless occupancy logic. |

## Basis-of-design equipment

| Qty | Element | Design basis |
| --- | --- | --- |
| 1+ | IPS-32 outputs | Corridor sections by floor/wing |
| 1+ | Zone controllers | Dimming by corridor section |
| Multiple | PIR sensors | Overlapping coverage along path of travel |
| 8 typ. | DC LED luminaires | Sectional zoning |

| EGRESS STAIRWELL | APPLICATION |
| --- | --- |

Application intent: Do not treat the stairwell like a conventional office zone; emergency operation and minimum illumination govern the design.

| CONTROL STRATEGIES | SEQUENCE OF OPERATION |
| --- | --- |
| Reduced standby level Occupancy raise Emergency-state coordination Continuous monitoring | Normal standby: fixtures remain at the approved minimum or full level required by the project. Presence: stairwell sensor raises the local or full stairwell zone to the occupied target. No presence: lighting returns to standby after the specified delay. Emergency / fire alarm: life-safety controls override normal energy-saving behavior as required. |

## Basis-of-design equipment

| Qty | Element | Design basis |
| --- | --- | --- |
| 1+ | IPS-32 outputs | Stairwell floors/sections as engineered |
| 1+ | Dimming controllers | Standby-to-full control |
| Multiple | PIR sensors | Landings and flights as needed |
| 6 typ. | DC LED luminaires | Listed/approved for application |

| ATRIUM / LOBBY | APPLICATION |
| --- | --- |

Application intent: Large public spaces are schedule- and scene-driven; occupancy is typically supplemental rather than the only control input.

| CONTROL STRATEGIES | SEQUENCE OF OPERATION |
| --- | --- |
| Multi-zone scene control Daylight harvesting Scheduling Occupancy assist Demand reduction ready | Open hours: schedule establishes the active scene and enables daylight trim near glazing. Occupied: lobby/atrium zones maintain their scene; local staff control can adjust approved zones. Bright daylight: perimeter/high-bay zones trim independently to preserve visual balance. Closed hours: schedule transitions to security/cleaning scene, then to the approved night state. |

## Basis-of-design equipment

| Qty | Element | Design basis |
| --- | --- | --- |
| 2+ | IPS-32 outputs/groups | Separate high-bay, perimeter, feature, and support zones |
| 3+ | Control channels | Scene-capable zone control |
| 1+ | PIR + ambient sensors | Used where sensor geometry is appropriate |
| 1+ | Self-powered wall controls | Staff scenes / override |
| 10+ | DC LED luminaires | Multiple architectural zones |

| COMPONENT REFERENCE | BASIS OF DESIGN |
| --- | --- |

# Key components in this guide

## EPS IPS-32 intelligent power distribution unit

32 outputs; 56 VDC; 100 W per output; software-controllable on/off/reset; output grouping; network/serial interfaces; remote monitoring. Use as the centralized branch-power platform.

## Casambi NASSR PDS-BAT-CAS sensor

Battery-powered PIR + ambient light sensor; Casambi 2.4 GHz BLE-based proprietary mesh; presence/absence scenarios; adjustable sensitivity and latency. Coordinate mounting height and coverage.

## mwConnect PSC-EO-WS BLE wall controller

Self-powered, batteryless Bluetooth wall control using an integrated micro-generator; supports manual on/off, wireless dimming, and scene/tunable-white functions depending on the paired controller.

## SmartDC-style room architecture

The uploaded SmartDC diagram illustrates a repeatable topology with low-voltage DC feeds plus control/network links to room controllers, PIR sensors, switches, relays, and receptacle interfaces. Use it as a topology reference, not a blanket wiring specification.

## IPS-32 configuration practices

Label each port by building/floor/room/zone.

Use port current and fault status for service diagnostics.

Use linked output groups only when simultaneous behavior is intended.

Set startup state deliberately for post-outage recovery.

Where multiple outputs are paralleled for a load, follow manufacturer instructions and project engineering.

| COMMISSIONING + HANDOFF | STARTUP |
| --- | --- |

# Room commissioning checklist

| ✓ | Item | Acceptance check |
| --- | --- | --- |
| ☐ | Power | Confirm correct IPS-32 port assignment, output voltage, polarity, branch protection, conductor sizing, and measured load current. |
| ☐ | Fixture control | Verify full on/off range, smooth dimming, minimum level, high-end trim, and zone mapping. |
| ☐ | Wall control | Pair/program the wall station; verify tap, press/hold, scene and override behavior. |
| ☐ | Occupancy | Verify sensor coverage, sensitivity, false-trigger resistance, timeout, and manual-on/auto-on policy. |
| ☐ | Daylight | Set target light level and confirm only intended perimeter/daylight zones respond. |
| ☐ | Schedules | Verify occupied, after-hours, holiday, cleaning and override behavior at the supervisory layer. |
| ☐ | Power recovery | Test IPS-32 startup state and controller/fixture recovery after loss and restoration of source power. |
| ☐ | BMS / API | Verify only the points and commands intended for integration; document ownership of overrides and priority. |
| ☐ | Documentation | Capture final device IDs, port labels, room names, scene levels, timeouts, setpoints, firmware/app versions and as-built changes. |

## Recommended project deliverables

Room application matrix and sequence of operation

DC one-line and branch schedule with IPS-32 port assignments

Reflected ceiling plan with sensor coverage and lighting zones

Control device schedule and compatibility matrix

Commissioning report with final setpoints and screenshots

BMS point list / API mapping where integrated

| REFERENCE BASIS + DESIGN NOTES | APPENDIX |
| --- | --- |

# Source materials used to develop this conceptual guide

## Lutron Commercial Applications Guide - 3672846

Used as the structural reference for a simple room-by-room application guide: overview, how-to-use, layouts, control functionality, strategies, and equipment schedules. The Symple guide uses original text and diagrams.

## Edge Power Solutions IPS-32 Gen3 specification

Basis for 32 x 56 VDC / 100 W outputs, intelligent grouping, network interfaces, monitoring, remote output control, protection, and startup/link configuration.

## Casambi / CUPOWER NASSR PDS-BAT-CAS specification

Basis for PIR + ambient light sensing, Casambi BLE mesh communication, battery operation, sensitivity/latency behavior, and coverage considerations.

## mwConnect PSC-EO-WS-BLE data sheet

Basis for self-powered batteryless Bluetooth wall control, wireless switching/dimming, scene/tunable-white capability, and wall mounting.

## SmartDC Lighting typical architecture diagram

Visual/topology reference for distributing 48-57 VDC and connecting room control/network devices; this guide does not assume every SmartDC conductor or controller detail applies to the EPS platform.

Engineering note: This guide is conceptual. Final designs must be reviewed against project lighting criteria, electrical code, energy code, emergency/egress requirements, applicable product listings, conductor ampacity/voltage-drop limits, environmental ratings, and the compatibility requirements of the selected controllers, sensors, luminaires and BMS gateway.